## The Parameter of PV array
Generally,the number of battery in one PV array is 60 or 72,Below form show PV array parameter on market,The technology parameter may has the difference on every manufactures ,please referece.
1. Monocrystalline silicon module 245-315W
Type | model（assume） | rated power | maximun power point voltage(Vmp) | maximun power point current(Imp) | open circuit voltage(Voc) | short-circuit current(Isc) | efficiency | Size | power error | Fuse capacity
60 pieces of battery | VOL-M-245W | 245W | 30.10V | 8.13A | 36.80V | 8.65A | 15.09% | 1640*990*40mm | 0+3% | 15A
| VOL-M-250W | 250W | 30.50V | 8.21A | 37.30V | 8.74A | 15.4% | 1640*990*40mm | 0+3% | 15A
| VOL-M-255W | 255W | 30.60V | 8.32A | 37.40V | 8.85A | 15.71% | 1640*990*40mm | 0+3% | 15A
| VOL-M-260W | 260W | 31.10V | 8.35A | 38.00V | 8.89A | 16.01% | 1640*990*40mm | 0+3% | 15A
| VOL-M-265W | 265W | 31.51V | 8.41A | 38.52V | 9.13A | 16.03% | 1640*990*40mm | 0+3% | 15A
72 pieces of battery | VOL-M-295W | 295W | 36.30V | 8.13A | 44.40V | 8.65A | 15.28% | 1640*990*50mm | 0+3% | 15A
| VOL-M-300W | 300W | 36.50V | 8.21A | 44.60V | 8.74A | 15.54% | 1640*990*50mm | 0+3% | 15A
| VOL-M-305W | 305W | 36.90V | 8.26A | 45.10V | 8.79A | 15.8% | 1640*990*50mm | 0+3% | 15A
| VOL-M-310W | 310W | 37.10V | 8.35A | 45.40V | 8.89A | 16.06% | 1640*990*50mm | 0+3% | 15A
| VOL-M-315W | 315W | 37.60V | 8.39A | 46.00V | 8.95A | 16.32% | 1640*990*50mm | 0+3% | 15A
2.Polysilicon module 240-305W
60 pieces of battery | VOL-P-240W | 240W | 30.00V | 8.00A | 35.70V | 8.57A | 14.78% | 1640*990*40mm | 0+3% | 15A
| VOL-P-245W | 245W | 30.40V | 8.05A | 36.10V | 8.63A | 15.09% | 1640*990*40mm | 0+3% | 15A
| VOL-P-250W | 250W | 30.60V | 8.17A | 36.30V | 8.71A | 15.4% | 1640*990*40mm | 0+3% | 15A
| VOL-P-255W | 255W | 30.70V | 8.30A | 36.40V | 8.80A | 15.71% | 1640*990*40mm | 0+3% | 15A
| VOL-P-260W | 260W | 30.90V | 8.42A | 36.70V | 8.89A | 16.01% | 1640*990*40mm | 0+3% | 15A
72 pieces of battery | VOL-P-285W | 285W | 35.90V | 7.94A | 42.70V | 8.51A | 14.76% | 1950*990*50mm | 0+3% | 15A
| VOL-P-290W | 290W | 36.30V | 8.00A | 43.20V | 8.57A | 15.02% | 1950*990*50mm | 0+3% | 15A
| VOL-P-295W | 295W | 36.50V | 8.08A | 43.30V | 8.64A | 15.28% | 1950*990*50mm | 0+3% | 15A
| VOL-P-300W | 300W | 36.70V | 8.17A | 43.60V | 8.71A | 15.54% | 1950*990*50mm | 0+3% | 15A
| VOL-P-305W | 305W | 43.70V | 8.27A | 49.50V | 8.78A | 15.8% | 1950*990*50mm | 0+3% | 15A
3.Monocrystalline silicon module 320-340W
72 pieces of battery | VOL-M-320W | 320W | 38.46V | 8.32A | 46.78V | 8.98A | 16.48% | 1960*991*40 | 0+3% | 15A
| VOL-M-325W | 325W | 38.55V | 8.43A | 46.95V | 9.07A | 16.73% | 1960*991*40 | 0+3% | 15A
| VOL-M-330W | 330W | 38.60V | 8.55A | 47.13V | 9.14A | 16.99% | 1960*991*40 | 0+3% | 15A
| VOL-M-335W | 335W | 38.68V | 8.66A | 47.28V | 9.23A | 17.25% | 1960*991*40 | 0+3% | 15A
| VOL-M-340W | 340W | 38.86V | 8.75A | 47.45V | 9.31A | 17.5% | 1960*991*40 | 0+3% | 15A
3.Polysilicon module 80-100W：
36 pieces of battery | VOL-P-80W | 80W | 17.4V | 4.60A | 21.6V | 5.14A | 16.2% | 880*664*30 | 0+3% | 10A
| VOL-P-85W | 85W | 17.5V | 4.86A | 21.7V | 5.37A | 17.1% | 880*664*30 | 0+3% | 10A
| VOL-P-90W | 90W | 17.6V | 5.12A | 21.8V | 5.58A | 15.8% | 998*664*30 | 0+3% | 10A
| VOL-P-95W | 95W | 17.8V | 5.34A | 21.9V | 5.78A | 16% | 998*664*30 | 0+3% | 10A
| VOL-P-100W | 100W | 17.4V | 5.75A | 21.7V | 6.31A | 15.2% | 1130*664*30 | 0+3% | 10A

## Recommended PV array
Fox example,output nominal voltage of water pump is 380V
Rated output power of ASPIRE | Type of PV array | model（assume） | the minimum cost combination type
2.2KW | Polysilicon 36pieces of battery | VOL-P-80W | 33 pieces series
|  | VOL-P-85W | 33pieces series
|  | VOL-P-90W | 33pieces series
|  | VOL-P-95W | 33pieces series
|  | VOL-P-100W | 33pieces series
7.5KW | Monocrystalline silicon 60 pieces of battery | VOL-M-245W | 19pieces series*2strings
|  | VOL-M-250W | 19pieces series*2strings
|  | VOL-M-255W | 19pieces series*2strings
|  | VOL-M-260W | 19pieces series*2strings
|  | VOL-M-265W | 19pieces series*2strings
| Monocrystalline silicon 72pieces of battery | VOL-M-295W | 16pieces series*2strings
|  | VOL-M-300W | 16pieces series*2strings
|  | VOL-M-305W | 16pieces series*2strings
|  | VOL-M-310W | 16pieces series*2strings
|  | VOL-M-315W | 16pieces series*2strings
| Monocrystalline silicon 72pieces of battery | VOL-M-320W | 15pieces series*2strings
|  | VOL-M-325W | 15pieces series*2strings
|  | VOL-M-330W | 15pieces series*2strings
|  | VOL-M-335W | 15pieces series*2strings
|  | VOL-M-340W | 15pieces series*2strings
| Polysilicon module36pieces of battery | VOL-P-90W | 33pieces series*3strings
|  | VOL-P-95W | 33pieces series*3strings
|  | VOL-P-100W | 33pieces series*3strings
| Polysilicon module60pieces of battery | VOL-P-240W | 19pieces series*2strings
|  | VOL-P-245W | 19pieces series*2strings
|  | VOL-P-250W | 19pieces series*2strings
|  | VOL-P-255W | 19pieces series*2strings
|  | VOL-P-260W | 19pieces series*2strings
| Polysilicon module72pieces of battery | VOL-P-285W | 16pieces series*2strings
|  | VOL-P-290W | 16pieces series*2strings
|  | VOL-P-295W | 16pieces series*2strings
|  | VOL-P-300W | 16pieces series*2strings
|  | VOL-P-305W | 14pieces series*2strings
11KW | Monocrystalline silicon60pieces of battery | VOL-M-245W | 19pieces series*3strings
|  | VOL-M-250W | 19pieces series*3strings
|  | VOL-M-255W | 19pieces series*3strings
|  | VOL-M-260W | 19pieces series*3strings
|  | VOL-M-265W | 19pieces series*3strings
| Monocrystalline silicon72pieces of battery | VOL-M-295W | 19pieces series*3strings
|  | VOL-M-300W | 19pieces series*3strings
|  | VOL-M-305W | 19pieces series*3strings
|  | VOL-M-310W | 18pieces series*3strings
|  | VOL-M-315W | 18pieces series*3strings
| Monocrystalline silicon72pieces of battery | VOL-M-320W | 15pieces series*3strings
|  | VOL-M-325W | 15pieces series*3strings
|  | VOL-M-330W | 15pieces series*3strings
|  | VOL-M-335W | 15pieces series*3strings
|  | VOL-M-340W | 15pieces series*3strings
| Polysilicon 60pieces of battery | VOL-P-240W | 19pieces series*3strings
|  | VOL-P-245W | 19pieces series*3strings
|  | VOL-P-250W | 19pieces series*3strings
|  | VOL-P-255W | 19pieces series*3strings
|  | VOL-P-260W | 19pieces series*3strings
| Polysilicon module72pieces of battery | VOL-P-285W | 16pieces series*3strings
|  | VOL-P-290W | 16pieces series*3strings
|  | VOL-P-295W | 16pieces series*3strings
|  | VOL-P-300W | 16pieces series*3strings
|  | VOL-P-305W | 14pieces series*3strings

## Caculation formula of PV array
PUMP INVERTER PV ARRAY CALCULATOR
Note：Customers just only key in parameter input in RED ZONE, and recommended PV array setup will show in BLUE ZONE automaticly
Known parameter: | Parameter input | Remark
Rated output power of ASPIRE(water pump) | 7500 | unit W（values 2200/7500/11000）
Nominal voltage of water pump | 380 | unit V（values 380/400/415/440）
PV array maximun power point voltage(Vmp) | 37.6 | unit V
PV array maximun power point current(Imp) | 12 | unit A
PV array open circuit voltage(Voc) | 46 | unit V
PV array short-circuit current(Isc) | 10.5 | unit A
PV array rated power | 315 | unit W
valuation:
Pieces of string(N) | 1.409
Pieces of series in one string(M) | 14.9021 | 17.3913
Result:
Number of Parallel strings (N) | 2
Number of Panels in series per string, Min value to Max value(M) | 15 | 17
PV array total power range(unit W) | 9450 | 10710